## icogen (hidden)
Cogeneration Penetration Estimation |  |  |  | Key: | Assumption
Changeable Assumptions in RED |  |  |  |  | Input
Calculation
This worksheet is used for data input only. The sample calculations in this worksheet are illustrative of how the cogen model
works, but will not match the detailed, regional model.
Dollar year for capital costs | 2018
Price Adjustments
Electricity Standby Charge (percent) | 10%
Max investment for full 10% ITC (In Energy Improvement and Extension Act, Title 1, Sec. 103( c) (3)(B)(ii) "applicable capacity") | 15000
ITC Phase-out (In Energy Improvement and Extension Act, Title 1, Sec. 103( c) (3)(B)(iii) "maximum capacity") | 50000
CapCostMultStar | 2008
CapCostMultEnd | 2024
Source: Leidos, Final Report: Distributed Generation, Battery Storage ,and Combined Heat and Power System Characteristics and Costs in the Buildings and Industrial Sectors, May 2020.
Reference Case (2018 data) | Table 5-4 | Table 26 | Table 27 | Table 27 | Table 27 | Table 27 | Table 27 | Table 28
| IC | IC | GT | GT | GT | GT | GT | Comb.Cyc (2 40MW GT & 20MW ST)
Cogen Cost & Performance Assumptions | System 1 NG Reciprocating Engine | System 2 NG Reciprocating Engine | System 3 NG Turbine | System 4 NG Turbine | System 5 NG Turbine | System 6 NG Turbine | System 7 Combined Cycle | System 8 Combined Cycle
Electricity Capacity (kw) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Change 2020 report
CapCostMult (1 - Investment Tax Credit) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | no change-research to change
Total Installed Cost (2018$/kw) w/o ITC | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Change 2020 report
Capacity Factor | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Change 2016 report
Overall Heat Rate (btus/kwh) (hhv) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Change 2020 report
Heatrate Multiplier, Alternate Assumption | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | no change
Heatrate, Alternate Assumption (btus/kwh) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | no change
Overall Efficiency | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Change 2020 report
Assumed captial cost mutliplier (first used in AEO2008), apply same rate to high technology parameters
| Reference | HiTech
15 percent increase | 1 | 1
The next 3 sections copy assumptions to yearly specifications which are read by the model.
The interpolation formulas can be replaced with actual values to model other time-specific assumptions.
Source: Leidos, Final Report: Distributed Generation, Battery Storage ,and Combined Heat and Power System Characteristics and Costs in the Buildings and Industrial Sectors, May 2020. | [9 empty] | Source: Leidos, Final Report: Distributed Generation, Battery Storage ,and Combined Heat and Power System Characteristics and Costs in the Buildings and Industrial Sectors, May 2020.
REFERENCE CASE | [9 empty] | RAPIC TECHNOLOGY DEVELOPMENT CASE
Cogen Cost & Performance Assumptions-by year | IC | IC | GT | GT | GT | GT | GT | Comb.Cyc (2 40MW GT & 20MW ST) |  | Cogen Cost & Performance Assumptions-by year | IC | IC | GT | GT | GT | GT | GT | Comb.Cyc (2 40MW GT & 20MW ST)
Total Installed Cost (2018$/kw) | System 1 NG Reciprocating Engine | System 2 NG Reciprocating Engine | System 3 NG Turbine | System 4 NG Turbine | System 5 NG Turbine | System 6 NG Turbine | System 7 Combined Cycle | System 8 Combined Cycle |  | Total Installed Cost (2005$/kw) | System 1 NG Reciprocating Engine | System 2 NG Reciprocating Engine | System 3 NG Turbine | System 4 NG Turbine | System 5 NG Turbine | System 6 NG Turbine | System 7 Combined Cycle | System 8 Combined Cycle
2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2015 | 1995.1369 | 1830.1888 | 1585.3931 | 1345.8506 | 1049.5744 | 863.6137 | 1674.6962 | 1674.6962 |  |  | Data from 2016 report that is 2015 | 0.95181 | 2015 | 2017
2016 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2016 | 1987 | 1823 | 1578 | 1339 | 1045 | 859 | 1663 | 1663
2017 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2017 | 1979 | 1816 | 1571 | 1333 | 1040 | 855 | 1651 | 1651
2018 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2018 | 1971 | 1809 | 1564 | 1327 | 1035 | 851 | 1639 | 1639
2019 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2019 | 1963 | 1802 | 1557 | 1321 | 1030 | 847 | 1627 | 1627
2020 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2020 | 1954.7018 | 1793.1255 | 1548.9038 | 1313.9682 | 1024.2452 | 842.2397 | 1616.6916 | 1616.6916 |  |  | Data from 2016 report that is 2015 | 1.0769 | 2020 | 2017
2021 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2021 | 1933 | 1773 | 1531 | 1299 | 1012 | 832 | 1594 | 1594
2022 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2022 | 1911 | 1753 | 1513 | 1284 | 1000 | 822 | 1571 | 1571
2023 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2023 | 1889 | 1733 | 1495 | 1269 | 988 | 812 | 1548 | 1548
2024 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2024 | 1867 | 1713 | 1477 | 1254 | 976 | 802 | 1525 | 1525
2025 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2025 | 1846.6798 | 1693.2002 | 1458.4667 | 1236.8651 | 963.5565 | 792.0204 | 1503.6077 | 1503.6077 |  |  | Data from 2016 report that is 2015 | 1.2184 | 2025 | 2017
2026 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2026 | 1833 | 1680 | 1447 | 1227 | 955 | 785 | 1490 | 1490
2027 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2027 | 1819 | 1667 | 1435 | 1217 | 947 | 778 | 1476 | 1476
2028 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2028 | 1805 | 1654 | 1423 | 1207 | 939 | 771 | 1462 | 1462
2029 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2029 | 1791 | 1641 | 1411 | 1197 | 931 | 764 | 1448 | 1448
2030 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2030 | 1776.5545 | 1629.2942 | 1399.3359 | 1186.0623 | 922.7347 | 758.7897 | 1433.4307 | 1433.4307 |  |  | Data from 2016 report that is 2015 | 1.3785 | 2030 | 2017
2031 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2031 | 1763 | 1617 | 1388 | 1176 | 915 | 752 | 1420 | 1420
2032 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2032 | 1750 | 1605 | 1377 | 1166 | 907 | 746 | 1407 | 1407
2033 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2033 | 1737 | 1593 | 1366 | 1156 | 899 | 740 | 1394 | 1394
2034 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2034 | 1724 | 1581 | 1355 | 1146 | 891 | 734 | 1381 | 1381
2035 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2035 | 1709.3483 | 1567.0095 | 1342.6014 | 1136.7872 | 884.1678 | 727.0821 | 1366.9657 | 1366.9657 |  |  | Data from 2016 report that is 2015 | 1.5597 | 2035 | 2017
2036 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2036 | 1696 | 1555 | 1332 | 1127 | 877 | 721 | 1352 | 1352
2037 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2037 | 1683 | 1543 | 1321 | 1118 | 870 | 715 | 1337 | 1337
2038 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2038 | 1670 | 1531 | 1310 | 1109 | 863 | 709 | 1322 | 1322
2039 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2039 | 1657 | 1519 | 1299 | 1100 | 856 | 703 | 1307 | 1307
2040 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2040 | 1644.5554 | 1507.4147 | 1288.1028 | 1090.3255 | 847.7791 | 697.0376 | 1294.3365 | 1294.3365 |  |  | Data from 2016 report that is 2015 | 1.7646 | 2040 | 2017
2041 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2041 | 1606 | 1472 | 1258 | 1065 | 828 | 681 | 1264 | 1264
2042 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2042 | 1568 | 1437 | 1228 | 1040 | 808 | 665 | 1234 | 1234
2043 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2043 | 1530 | 1402 | 1198 | 1015 | 788 | 649 | 1204 | 1204
2044 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2044 | 1492 | 1367 | 1168 | 990 | 768 | 633 | 1174 | 1174
2045 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2045 | 1453.5473 | 1332.3349 | 1138.4952 | 963.6889 | 749.3132 | 616.0797 | 1144.0049 | 1144.0049 |  |  | Data from 2016 report that is 2015 | 1.9965 | 2045 | 2017
2046 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2046 | 1420 | 1301 | 1112 | 941 | 732 | 602 | 1117 | 1117
2047 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2047 | 1386 | 1270 | 1086 | 919 | 715 | 588 | 1090 | 1090
2048 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2048 | 1352 | 1239 | 1060 | 897 | 698 | 574 | 1063 | 1063
2049 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2049 | 1318 | 1208 | 1034 | 875 | 681 | 560 | 1036 | 1036
2050 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2050 | 1284.724 | 1177.5899 | 1006.2639 | 851.7605 | 662.2837 | 544.5247 | 1011.1336 | 1011.1336 |  |  | Data from 2016 report that is 2015 | 2.2589 | 2050 | 2017
| IC | IC | GT | GT | GT | GT | GT | Comb.Cyc (2 40MW GT & 20MW ST) |  |  | IC | IC | GT | GT | GT | GT | GT | Comb.Cyc (2 40MW GT & 20MW ST)
Overall Heat Rate (btus/kwh) (hhv) | System 1 NG Reciprocating Engine | System 2 NG Reciprocating Engine | System 3 NG Turbine | System 4 NG Turbine | System 5 NG Turbine | System 6 NG Turbine | System 7 Combined Cycle | System 8 Combined Cycle |  | Overall Heat Rate (btus/kwh) (hhv) | System 1 NG Reciprocating Engine | System 2 NG Reciprocating Engine | System 3 NG Turbine | System 4 NG Turbine | System 5 NG Turbine | System 6 NG Turbine | System 7 Combined Cycle | System 8 Combined Cycle
2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2015 | 9614 | 7810 | 12688 | 12037 | 10189 | 9305 | 8353 | 8353 |  |  | Data from 2016 report
2016 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2016 | 9571 | 7775 | 12613 | 11966 | 10189 | 9305 | 8199 | 8199
2017 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2017 | 9528 | 7740 | 12538 | 11895 | 10189 | 9305 | 8045 | 8045
2018 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2018 | 9485 | 7705 | 12463 | 11824 | 10189 | 9305 | 7891 | 7891
2019 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2019 | 9442 | 7670 | 12388 | 11753 | 10189 | 9305 | 7737 | 7737
2020 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2020 | 9398 | 7635 | 12311 | 11680 | 10189 | 9305 | 7584 | 7584 |  |  | Data from 2016 report
2021 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2021 | 9393 | 7631 | 12287 | 11657 | 10128 | 9250 | 7432 | 7432
2022 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2022 | 9388 | 7627 | 12263 | 11634 | 10067 | 9195 | 7280 | 7280
2023 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2023 | 9383 | 7623 | 12239 | 11611 | 10006 | 9140 | 7128 | 7128
2024 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2024 | 9378 | 7619 | 12215 | 11588 | 9945 | 9085 | 6976 | 6976
2025 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2025 | 9375 | 7616 | 12189 | 11564 | 9886 | 9029 | 6826 | 6826 |  |  | Data from 2016 report
2026 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2026 | 9370 | 7612 | 12165 | 11541 | 9866 | 9011 | 6702 | 6702
2027 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2027 | 9365 | 7608 | 12141 | 11518 | 9846 | 8993 | 6578 | 6578
2028 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2028 | 9360 | 7604 | 12117 | 11495 | 9826 | 8975 | 6454 | 6454
2029 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2029 | 9355 | 7600 | 12093 | 11472 | 9806 | 8957 | 6330 | 6330
2030 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2030 | 9351 | 7597 | 12069 | 11449 | 9788 | 8939 | 6205 | 6205 |  |  | Data from 2016 report
2031 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2031 | 9347 | 7593 | 12045 | 11426 | 9769 | 8921 | 6102 | 6102
2032 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2032 | 9343 | 7589 | 12021 | 11403 | 9750 | 8903 | 5999 | 5999
2033 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2033 | 9339 | 7585 | 11997 | 11380 | 9731 | 8885 | 5896 | 5896
2034 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2034 | 9335 | 7581 | 11973 | 11357 | 9712 | 8867 | 5793 | 5793
2035 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2035 | 9329 | 7577 | 11949 | 11336 | 9691 | 8850 | 5688 | 5688 |  |  | Data from 2016 report
2036 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2036 | 9324 | 7573 | 11925 | 11313 | 9672 | 8833 | 5688 | 5688
2037 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2037 | 9319 | 7569 | 11901 | 11290 | 9653 | 8816 | 5688 | 5688
2038 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2038 | 9314 | 7565 | 11877 | 11267 | 9634 | 8799 | 5688 | 5688
2039 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2039 | 9309 | 7561 | 11853 | 11244 | 9615 | 8782 | 5688 | 5688
2040 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2040 | 9305 | 7559 | 11831 | 11223 | 9595 | 8763 | 5688 | 5688 |  |  | Data from 2016 report
2041 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2041 | 9300 | 7555 | 11808 | 11201 | 9576 | 8746 | 5688 | 5688
2042 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2042 | 9295 | 7551 | 11785 | 11179 | 9557 | 8729 | 5688 | 5688
2043 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2043 | 9290 | 7547 | 11762 | 11157 | 9538 | 8712 | 5688 | 5688
2044 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2044 | 9285 | 7543 | 11739 | 11135 | 9519 | 8695 | 5688 | 5688
2045 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2045 | 9281 | 7541 | 11714 | 11111 | 9500 | 8677 | 5688 | 5688 |  |  | NEW DATA same percent change
2046 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2046 | 9276 | 7537 | 11691 | 11089 | 9481 | 8660 | 5688 | 5688
2047 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2047 | 9271 | 7533 | 11668 | 11067 | 9462 | 8643 | 5688 | 5688
2048 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2048 | 9266 | 7529 | 11645 | 11045 | 9443 | 8626 | 5688 | 5688
2049 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2049 | 9261 | 7525 | 11622 | 11023 | 9424 | 8609 | 5688 | 5688
2050 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2050 | 9257 | 7523 | 11598 | 11000 | 9406 | 8592 | 5688 | 5688 |  |  | NEW DATA same percent change
| IC | IC | GT | GT | GT | GT | GT | Comb.Cyc (2 40MW GT & 20MW ST) |  |  | IC | IC | GT | GT | GT | GT | GT | Comb.Cyc (2 40MW GT & 20MW ST)
Overall Efficiency | System 1 NG Reciprocating Engine | System 2 NG Reciprocating Engine | System 3 NG Turbine | System 4 NG Turbine | System 5 NG Turbine | System 6 NG Turbine | System 7 Combined Cycle | System 8 Combined Cycle |  | Overall Efficiency | System 1 NG Reciprocating Engine | System 2 NG Reciprocating Engine | System 3 NG Turbine | System 4 NG Turbine | System 5 NG Turbine | System 6 NG Turbine | System 7 Combined Cycle | System 8 Combined Cycle
2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2015 | 0.785 | 0.858 | 0.684 | 0.7035 | 0.744 | 0.692 | 0.485 | 0.485 |  |  | Data from 2016 report
2016 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2016 | 0.7866 | 0.8619 | 0.6856 | 0.7052 | 0.7362 | 0.692 | 0.4933 | 0.4933
2017 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2017 | 0.7882 | 0.8658 | 0.6872 | 0.7069 | 0.7284 | 0.692 | 0.5016 | 0.5016
2018 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2018 | 0.7898 | 0.8697 | 0.6888 | 0.7086 | 0.7206 | 0.692 | 0.5099 | 0.5099
2019 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2019 | 0.7914 | 0.8736 | 0.6904 | 0.7103 | 0.7128 | 0.692 | 0.5182 | 0.5182
2020 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2020 | 0.7932 | 0.8776 | 0.6922 | 0.7122 | 0.705 | 0.692 | 0.5264 | 0.5264 |  |  | Data from 2016 report
2021 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2021 | 0.7934 | 0.8778 | 0.6928 | 0.7128 | 0.707 | 0.6942 | 0.5364 | 0.5364
2022 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2022 | 0.7936 | 0.878 | 0.6934 | 0.7134 | 0.709 | 0.6964 | 0.5464 | 0.5464
2023 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2023 | 0.7938 | 0.8782 | 0.694 | 0.714 | 0.711 | 0.6986 | 0.5564 | 0.5564
2024 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2024 | 0.794 | 0.8784 | 0.6946 | 0.7146 | 0.713 | 0.7008 | 0.5664 | 0.5664
2025 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2025 | 0.7941 | 0.8788 | 0.695 | 0.7151 | 0.7152 | 0.7032 | 0.5764 | 0.5764 |  |  | Data from 2016 report
2026 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2026 | 0.7943 | 0.879 | 0.6956 | 0.7157 | 0.7159 | 0.704 | 0.5864 | 0.5864
2027 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2027 | 0.7945 | 0.8792 | 0.6962 | 0.7163 | 0.7166 | 0.7048 | 0.5964 | 0.5964
2028 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2028 | 0.7947 | 0.8794 | 0.6968 | 0.7169 | 0.7173 | 0.7056 | 0.6064 | 0.6064
2029 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2029 | 0.7949 | 0.8796 | 0.6974 | 0.7175 | 0.718 | 0.7064 | 0.6164 | 0.6164
2030 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2030 | 0.795 | 0.8799 | 0.6978 | 0.7181 | 0.7187 | 0.707 | 0.6264 | 0.6264 |  |  | Data from 2016 report
2031 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2031 | 0.7952 | 0.8801 | 0.6984 | 0.7187 | 0.7194 | 0.7078 | 0.6364 | 0.6364
2032 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2032 | 0.7954 | 0.8803 | 0.699 | 0.7193 | 0.7201 | 0.7086 | 0.6464 | 0.6464
2033 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2033 | 0.7956 | 0.8805 | 0.6996 | 0.7199 | 0.7208 | 0.7094 | 0.6564 | 0.6564
2034 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2034 | 0.7958 | 0.8807 | 0.7002 | 0.7205 | 0.7215 | 0.7102 | 0.6664 | 0.6664
2035 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2035 | 0.7959 | 0.8811 | 0.7006 | 0.7211 | 0.7222 | 0.7108 | 0.6764 | 0.6764 |  |  | Data from 2016 report
2036 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2036 | 0.7961 | 0.8813 | 0.7012 | 0.7217 | 0.7229 | 0.7116 | 0.6764 | 0.6764
2037 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2037 | 0.7963 | 0.8815 | 0.7018 | 0.7223 | 0.7236 | 0.7124 | 0.6764 | 0.6764
2038 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2038 | 0.7965 | 0.8817 | 0.7024 | 0.7229 | 0.7243 | 0.7132 | 0.6764 | 0.6764
2039 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2039 | 0.7967 | 0.8819 | 0.703 | 0.7235 | 0.725 | 0.714 | 0.6764 | 0.6764
2040 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2040 | 0.7968 | 0.8822 | 0.7035 | 0.7241 | 0.7257 | 0.7147 | 0.6764 | 0.6764 |  |  | Data from 2016 report
2041 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2041 | 0.797 | 0.8824 | 0.7041 | 0.7247 | 0.7264 | 0.7155 | 0.6764 | 0.6764
2042 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2042 | 0.7972 | 0.8826 | 0.7047 | 0.7253 | 0.7271 | 0.7163 | 0.6764 | 0.6764
2043 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2043 | 0.7974 | 0.8828 | 0.7053 | 0.7259 | 0.7278 | 0.7171 | 0.6764 | 0.6764
2044 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2044 | 0.7976 | 0.883 | 0.7059 | 0.7265 | 0.7285 | 0.7179 | 0.6764 | 0.6764
2045 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2045 | 0.7977 | 0.8833 | 0.7064 | 0.7271 | 0.7292 | 0.7186 | 0.6764 | 0.6764 |  |  | NEW DATA same percent change
2046 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2046 | 0.7979 | 0.8835 | 0.707 | 0.7277 | 0.7299 | 0.7194 | 0.6764 | 0.6764
2047 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2047 | 0.7981 | 0.8837 | 0.7076 | 0.7283 | 0.7306 | 0.7202 | 0.6764 | 0.6764
2048 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2048 | 0.7983 | 0.8839 | 0.7082 | 0.7289 | 0.7313 | 0.721 | 0.6764 | 0.6764
2049 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2049 | 0.7985 | 0.8841 | 0.7088 | 0.7295 | 0.732 | 0.7218 | 0.6764 | 0.6764
2050 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2050 | 0.7986 | 0.8844 | 0.7093 | 0.7301 | 0.7328 | 0.7226 | 0.6764 | 0.6764 |  |  | NEW DATA same percent change
Market Penetration Assumptions | Industrial | IPP Version | source: | L:\mid\Industrial_Team\US\AEO\AEO2018\CHP\indcogen\payback acceptance.xlsx
Payback Acceptance Fraction | (smaller plants) | (large plants)
Payback Years | Fraction with a given payback need |  |  |  |  | temp storage
0 | 0% | 0% |  |  |  | 0%
1 | 13.8% | 13.8% |  |  |  | 10%
2 | 13.34% | 13.34% |  |  |  | 12%
3 | 12.77% | 12.77% |  |  |  | 13%
4 | 12% | 12% |  |  |  | 14%
5 | 11.02% | 11.02% |  |  |  | 13%
6 | 9.856% | 9.856% |  |  |  | 12%
7 | 8.531% | 8.531% |  |  |  | 9%
8 | 7.063% | 7.063% |  |  |  | 8%
9 | 5.478% | 5.478% |  |  |  | 5%
10 | 3.801% | 3.801% |  |  |  | 3%
11 | 2.061% | 2.061% |  |  |  | 1%
12 | 0.2869% | 0.2869% |  |  |  | 0%
leave blank==> | 0% | 0%
Check: Should add to 100% ==> | 100% | 100%
Fraction with this payback or longer
0 | 100% | 100% | [7 empty] | Change Calculation to sum
1 | 100% | 100%
2 | 86.2% | 86.2%
3 | 72.86% | 72.86%
4 | 60.09% | 60.09%
5 | 48.1% | 48.1%
6 | 37.08% | 37.08%
7 | 27.22% | 27.22%
8 | 18.69% | 18.69%
9 | 11.63% | 11.63%
10 | 6.149% | 6.149%
11 | 2.348% | 2.348%
12 | 0.2869% | 0.2869%
leave blank==> | 0% | 0%
Yearly penetration fraction | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
[5 empty] | 0.40941 | 0.59059 | <==ADL Frac (250-500)/(>250 all)
Capacity by Industry/Size | Sources: GRI, Characterization of the U.S. Industrial Commercial Boiler Population (and ADL's study of ABMA data (1995 Study) for 250-500 frac)
| 1.5-10 mmbtu/hr | 10-50 mmbtu/hr | 50-100mmbtu/hr | 100-250 mmbtu/hr | 250-500 mmbtu/hr | >500mmbtu | Total |  | >250 | [7 empty] | Boiler Data for Graph--Divided by 1000
Food | 31070 | 64970 | 37885 | 47950 | 11406.0445 | 16453.9555 | 209735 |  | 27860 | [7 empty] | 64.97 | 37.885 | 47.95 | 11.406
Paper | 4105 | 24490 | 36665 | 81500 | 93995.4685 | 135594.5315 | 376350 |  | 229590 | [7 empty] | 24.49 | 36.665 | 81.5 | 93.9955
Chemicals | 28660 | 81690 | 64970 | 86840 | 61785.4703 | 89129.5297 | 413075 |  | 150915 | [7 empty] | 81.69 | 64.97 | 86.84 | 61.7855
Primary Metals | 7505 | 19405 | 22585 | 17775 | 18572.6923 | 26792.3077 | 112635 |  | 45365 | [7 empty] | 19.405 | 22.585 | 17.775 | 18.5727
Other Manuf | 29710 | 80585 | 62630 | 62790 | 19553.2191 | 28206.7809 | 283475 |  | 47760 | [7 empty] | 80.585 | 62.63 | 62.79 | 19.5532
Refining | 1255 | 6670 | 18390 | 30480 | 46967.0288 | 67752.9712 | 171515 |  | 114720
Total | 102305 | 277810 | 243125 | 327335 | 252279.9234 | 363930.0766 | 1566785 |  | 616210
Number of units | 23495 | 12380 | 3570 | 2210 | 776.2459 | 583.7541 | 42431.2459 |  | 1360
Average Boiler Size (mmbtu/hr) | 4.3543 | 22.4402 | 68.1022 | 148.1154 | 325 | 623.4305 | 36.9253
Steam Load Segmentation (Based on Boiler distribution above)
Fraction of Boilers by Size | 1.5 - 3 mmbtu/hr | 3 - 6.5 /mmbtu | 6.5 - 10 mmbtu/hr | 10-50 mmbtu/hr | 50-100mmbtu/hr | 100-250 mmbtu/hr | 250-500 mmbtu/hr | >500mmbtu | Total
Food | 4.937% | 4.937% | 4.937% | 30.98% | 18.06% | 22.86% | 5.438% | 7.845% | 100%
Paper | 0.3635% | 0.3635% | 0.3635% | 6.507% | 9.742% | 21.66% | 24.98% | 36.03% | 100%
Chemicals | 2.313% | 2.313% | 2.313% | 19.78% | 15.73% | 21.02% | 14.96% | 21.58% | 100%
Primary Metals | 2.221% | 2.221% | 2.221% | 17.23% | 20.05% | 15.78% | 16.49% | 23.79% | 100%
Other Manuf | 3.493% | 3.493% | 3.493% | 28.43% | 22.09% | 22.15% | 6.898% | 9.95% | 100%
Refining | 0.2439% | 0.2439% | 0.2439% | 3.889% | 10.72% | 17.77% | 27.38% | 39.5% | 100%
All (average) | 2.176% | 2.176% | 2.176% | 17.73% | 15.52% | 20.89% | 16.1% | 23.23% | 100%

## Charts
Figure 6 4. U.S. average industrial CHP system capital costs ($/kW-AC, 2022 $)
Year | Reciprocating Engine (1 MW-AC) | Reciprocating Engine (3 MW-AC) | Gas Turbine (5 MW-AC) | Gas Turbine (10 MW-AC) | Gas Turbine (25 MW-AC) | Gas Turbine (40 MW-AC) | Combined Cycle (100 MW-AC) | Combined Cycle (375 MW-AC)
2015 | 3182.0016 | 2799.8 | 3350.625 | 2509.52 | 1927.86 | 1584.96 | 1765.12 | 1426.88
2018 | 3151.115 | 2783.795 | 2947.168 | 2119.4072 | 1731.65 | 1505.2829 | 1753.5448 | 1406.1972
2019 | 3143.6 | 2778.2 | 2818.8 | 2115.1981 | 1728.0554 | 1502.165 | 1743.5787 | 1404.6118
2020 | 3136.7321 | 2736.0694 | 2747.4141 | 2079.6464 | 1716.3444 | 1481.7781 | 1732.64 | 1400.7778
2021 | 3129.8642 | 2693.9387 | 2676.0282 | 2044.0948 | 1704.6334 | 1461.3912 | 1682.3712 | 1391.6655
2022 | 3125.2856 | 2585.8516 | 2628.4376 | 2020.3937 | 1696.8261 | 1447.8 | 1632.1024 | 1382.5531
Figure 6 6. U.S. average industrial CHP system O&M costs ($/kWh)
year | Reciprocating Engine (1 MW-AC) | Reciprocating Engine (3 MW-AC) | Gas Turbine (5 MW-AC) | Gas Turbine (10 MW-AC) | Gas Turbine (25 MW-AC) | Gas Turbine (40 MW-AC) | Combined Cycle (100 MW-AC) | Combined Cycle (375 MW-AC)
2015 | 0.021503 | 0.018108 | 0.017344 | 0.015164 | 0.011165 | 0.011063 | 0.0048409 | 0.0037752
2018 | 0.02244 | 0.018899 | 0.01734 | 0.01516 | 0.011162 | 0.01106 | 0.0048397 | 0.0037743
2019 | 0.02242 | 0.01888 | 0.017168 | 0.014132 | 0.010599 | 0.01058 | 0.0046297 | 0.0036105
2020 | 0.021344 | 0.017837 | 0.016394 | 0.014069 | 0.010605 | 0.010585 | 0.004632 | 0.0036123
2021 | 0.020268 | 0.016795 | 0.01562 | 0.014005 | 0.010611 | 0.010571 | 0.004626 | 0.0036076
2022 | 0.01955 | 0.0161 | 0.01464 | 0.013051 | 0.010104 | 0.010096 | 0.004418 | 0.0034455

## Summary_Tables
Technology | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Sector | Industrial
Equipment | Total
Vintage | New
Year | 2022
Dollar Year | 2022
Size, Technology, & Configuration | Small_Recip_CHP | Large_Recip_CHP | Med_GT_CHP | Large1_GT_CHP | Large2_GT_CHP | Large3_GT_CHP | Small_CC_CHP | Large_CC_CHP | Small_Storage_Ind | Med_Storage_Ind | Large_Storage_Ind
Prime Mover | Reciprocating Engine | Reciprocating Engine | Gas Turbine | Gas Turbine | Gas Turbine | Gas Turbine | Combined Cycle | Combined Cycle | Battery Storage | Battery Storage | Battery Storage
Fuel Type | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Grid Power | Grid Power | Grid Power
Output Capacity (kW) | 1000 | 3000 | 5000 | 10000 | 25000 | 40000 | 100000 | 375000 | 100 | 500 | 1000
Energy Capacity (MWh) | - | - | - | - | - | - | - | - | 400 | 2000 | 4000
Capacity Factor (%) | 91.32% | 91.32% | 91.32% | 91.32% | 93.61% | 93.61% | 93.61% | 93.61% | - | - | -
Hours of Operation (hrs) | 8000 | 8000 | 8000 | 8000 | 8200 | 8200 | 8200 | 8200 | - | - | -
Electric Heat Rate, HHV (Btu/kWh) | 9210.3391 | 8417.139 | 12184.8439 | 12090.7158 | 9720.1498 | 9610.7262 | 6748.9542 | 6245.6606 | - | - | -
Electric Efficiency, HHV (%) | 36.8% | 40.4% | 28% | 28.22% | 34.21% | 35.5% | 50.56% | 54.63% | - | - | -
Fuel Input (Btu/hr) | 9210.3391 | 25251.4169 | 60924.2197 | 120907.158 | 243003.7458 | 384429.0463 | 674895.4198 | 2342122.7201 | - | - | -
Thermal Output (Btu/hr) | 3890 | 9680 | 27414.6601 | 58338.2531 | 83973.6348 | 132003.2062 | 341225.9259 | 683247 | - | - | -
Total CHP Efficiency, HHV (%) | 78.7% | 78.8% | 68.8% | 68.4% | 69.3% | 70.3% | 65.54% | 63.27% | - | - | -
Power-to-Heat Ratio | 0.89 | 1.06 | 0.58 | 0.7 | 0.9 | 1.03 | 1.6 | 1.88 | - | - | -
Net Heat Rate (Btu/kWh) | 4335.4511 | 4329.9492 | 5016.9093 | 4988.2968 | 4878.4673 | 4853.4851 | 5206.2716 | 4097.2029 | - | - | -
Equipment Lifetime (years) | 25 | 25 | 30 | 30 | 30 | 30 | 35 | 35 | - | - | -
Inverter Life (years) | - | - | - | - | - | - | - | - | 15 | 15 | 15
Cycles per Day | - | - | - | - | - | - | - | - | 1 | 1 | 1
Annual Energy Degradation | - | - | - | - | - | - | - | - | 0.5% | 0.5% | 0.5%
Battery Cell Life (years) | - | - | - | - | - | - | - | - | 10 | 10 | 10
Total Installed Cost ($/kW) | 3125.2856 | 2585.8516 | 2628.4376 | 2020.3937 | 1696.8261 | 1447.8 | 1632.1024 | 1382.5531 | 3034.4093 | 2637.9166 | 2276.4918
Equipment Cost ($/kW) | 1452.0383 | 1151.1252 | 1067.0309 | 925.2113 | 734.4655 | 614.81 | 591.6963 | 489.8447 | 1546.0436 | 1428.6851 | 1503.6231
BOP & Installation ($/kW) | 1673.2473 | 1434.7264 | 1561.4066 | 1095.1824 | 962.3606 | 832.99 | 1040.4061 | 892.7084 | 1488.3657 | 1209.2314 | 772.8687
Variable O&M Costs ($/kWh) | 0.01955 | 0.0161 | 0.01464 | 0.013051 | 0.010104 | 0.010096 | 0.004418 | 0.0034455 | - | - | -
Fixed O&M Costs ($/kW-year) | - | - | - | - | - | - | - | - | 75.8602 | 65.9479 | 56.9123
Sector | Industrial
Equipment | Total
Vintage | New
Year | 2021
Dollar Year | 2022
Size, Technology, & Configuration | Small_Recip_CHP | Large_Recip_CHP | Med_GT_CHP | Large1_GT_CHP | Large2_GT_CHP | Large3_GT_CHP | Small_CC_CHP | Large_CC_CHP | Small_Storage_Ind | Med_Storage_Ind | Large_Storage_Ind
Prime Mover | Reciprocating Engine | Reciprocating Engine | Gas Turbine | Gas Turbine | Gas Turbine | Gas Turbine | Combined Cycle | Combined Cycle | Battery Storage | Battery Storage | Battery Storage
Fuel Type | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Grid Power | Grid Power | Grid Power
Output Capacity (kW) | 1000 | 3000 | 5000 | 10000 | 25000 | 40000 | 100000 | 375000 | 100 | 500 | 1000
Energy Capacity (MWh) | - | - | - | - | - | - | - | - | 400 | 2000 | 4000
Capacity Factor (%) | 91.32% | 91.32% | 91.32% | 91.32% | 93.61% | 93.61% | 93.61% | 93.61% | - | - | -
Hours of Operation (hrs) | 8000 | 8000 | 8000 | 8000 | 8200 | 8200 | 8200 | 8200 | - | - | -
Electric Heat Rate, HHV (Btu/kWh) | 9210.3391 | 8417.139 | 12184.8439 | 12129.3992 | 9980.2586 | 9617.7749 | 6758.824 | 6254.478 | - | - | -
Electric Efficiency, HHV (%) | 36.8% | 40.4% | 28% | 28.13% | 34.19% | 35.48% | 50.48% | 54.55% | - | - | -
Fuel Input (Btu/hr) | 9210.3391 | 25251.4169 | 60924.2197 | 121293.9922 | 249506.4639 | 384710.997 | 675882.401 | 2345429.2513 | - | - | -
Thermal Output (Btu/hr) | 3885 | 9695 | 27443.9791 | 58708.0921 | 84134.7449 | 132112.4834 | 342413.8919 | 684162.24 | - | - | -
Total CHP Efficiency, HHV (%) | 78.7% | 78.8% | 68.8% | 68.3% | 69.3% | 70.25% | 65.51% | 63.26% | - | - | -
Power-to-Heat Ratio | 0.89 | 1.06 | 0.58 | 0.7 | 0.9 | 1.03 | 1.6 | 1.87 | - | - | -
Net Heat Rate (Btu/kWh) | 4335.4511 | 4329.9492 | 5029.1105 | 4995.604 | 4878.4673 | 4856.9395 | 5208.2132 | 4097.7746 | - | - | -
Equipment Lifetime (years) | 25 | 25 | 30 | 30 | 30 | 30 | 35 | 35 | - | - | -
Inverter Life (years) | - | - | - | - | - | - | - | - | 15 | 15 | 15
Cycles per Day | - | - | - | - | - | - | - | - | 1 | 1 | 1
Annual Energy Degradation | - | - | - | - | - | - | - | - | 0.5% | 0.5% | 0.5%
Battery Cell Life (years) | - | - | - | - | - | - | - | - | 10 | 10 | 10
Total Installed Cost ($/kW) | 3129.8642 | 2693.9387 | 2676.0282 | 2044.0948 | 1704.6334 | 1461.3912 | 1682.3712 | 1391.6655 | 2887.5257 | 2472.2903 | 2129.502
Equipment Cost ($/kW) | 1497.9287 | 1183.3439 | 1061.2732 | 903.0595 | 737.3525 | 620.5816 | 608.3281 | 493.3031 | 1409.0819 | 1329.1686 | 1398.8867
BOP & Installation ($/kW) | 1631.9355 | 1510.5948 | 1614.755 | 1141.0353 | 967.2809 | 840.8097 | 1074.043 | 898.3624 | 1478.4438 | 1143.1217 | 730.6153
Variable O&M Costs ($/kWh) | 0.020268 | 0.016795 | 0.01562 | 0.014005 | 0.010611 | 0.010571 | 0.004626 | 0.0036076 | - | - | -
Fixed O&M Costs ($/kW-year) | - | - | - | - | - | - | - | - | 72.1881 | 61.8073 | 53.2376
Sector | Industrial
Equipment | Total
Vintage | New
Year | 2020
Dollar Year | 2022
Size, Technology, & Configuration | Small_Recip_CHP | Large_Recip_CHP | Med_GT_CHP | Large1_GT_CHP | Large2_GT_CHP | Large3_GT_CHP | Small_CC_CHP | Large_CC_CHP | Small_Storage_Ind | Med_Storage_Ind | Large_Storage_Ind
Prime Mover | Reciprocating Engine | Reciprocating Engine | Gas Turbine | Gas Turbine | Gas Turbine | Gas Turbine | Combined Cycle | Combined Cycle | Battery Storage | Battery Storage | Battery Storage
Fuel Type | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Grid Power | Grid Power | Grid Power
Output Capacity (kW) | 1000 | 3000 | 5000 | 10000 | 25000 | 40000 | 100000 | 375000 | 100 | 500 | 1000
Energy Capacity (MWh) | - | - | - | - | - | - | - | - | 400 | 2000 | 4000
Capacity Factor (%) | 91.32% | 91.32% | 91.32% | 91.32% | 93.61% | 93.61% | 93.61% | 93.61% | - | - | -
Hours of Operation (hrs) | 8000 | 8000 | 8000 | 8000 | 8200 | 8200 | 8200 | 8200 | - | - | -
Electric Heat Rate, HHV (Btu/kWh) | 9210.3391 | 8417.139 | 12184.8439 | 12077.8761 | 9985.3673 | 9624.8237 | 6768.1411 | 6269.2954 | - | - | -
Electric Efficiency, HHV (%) | 36.8% | 40.4% | 27.92% | 28.25% | 34.17% | 35.45% | 50.41% | 54.42% | - | - | -
Fuel Input (Btu/hr) | 9210.3391 | 25251.4169 | 60924.2197 | 120778.7611 | 249634.182 | 384992.9478 | 676814.1111 | 2350985.7825 | - | - | -
Thermal Output (Btu/hr) | 3880 | 9710 | 27497.3046 | 58802.9357 | 84295.8551 | 132221.7606 | 343601.858 | 685104 | - | - | -
Total CHP Efficiency, HHV (%) | 78.7% | 78.8% | 68.8% | 68.2% | 69.3% | 70.21% | 65.5% | 63.25% | - | - | -
Power-to-Heat Ratio | 0.88 | 1.06 | 0.58 | 0.7 | 0.9 | 1.03 | 1.6 | 1.87 | - | - | -
Net Heat Rate (Btu/kWh) | 4335.4511 | 4329.9492 | 5041.3712 | 5002.9326 | 4879.1649 | 4859.7066 | 5209.1548 | 4098.258 | - | - | -
Equipment Lifetime (years) | 25 | 25 | 30 | 30 | 30 | 30 | 35 | 35 | - | - | -
Inverter Life (years) | - | - | - | - | - | - | - | - | 15 | 15 | 15
Cycles per Day | - | - | - | - | - | - | - | - | 1 | 1 | 1
Annual Energy Degradation | - | - | - | - | - | - | - | - | 0.5% | 0.5% | 0.5%
Battery Cell Life (years) | - | - | - | - | - | - | - | - | 10 | 10 | 10
Total Installed Cost ($/kW) | 3136.7321 | 2736.0694 | 2747.4141 | 2079.6464 | 1716.3444 | 1481.7781 | 1732.64 | 1400.7778 | 3147.534 | 2646.5802 | 2472.2903
Equipment Cost ($/kW) | 1566.7644 | 1171.6719 | 1052.6366 | 869.8319 | 741.6829 | 629.2389 | 624.96 | 496.7615 | 1609.967 | 1482.696 | 1385.0534
BOP & Installation ($/kW) | 1569.9677 | 1564.3974 | 1694.7775 | 1209.8146 | 974.6615 | 852.5392 | 1107.68 | 904.0164 | 1537.5669 | 1163.8843 | 1087.2369
Variable O&M Costs ($/kWh) | 0.021344 | 0.017837 | 0.016394 | 0.014069 | 0.010605 | 0.010585 | 0.004632 | 0.0036123 | - | - | -
Fixed O&M Costs ($/kW-year) | - | - | - | - | - | - | - | - | 78.6883 | 66.1645 | 61.8073
Sector | Industrial
Equipment | Total
Vintage | New
Year | 2019
Dollar Year | 2022
Size, Technology, & Configuration | Small_Recip_CHP | Large_Recip_CHP | Med_GT_CHP | Large1_GT_CHP | Large2_GT_CHP | Large3_GT_CHP | Small_CC_CHP | Large_CC_CHP | Small_Storage_Ind | Med_Storage_Ind | Large_Storage_Ind
Prime Mover | Reciprocating Engine | Reciprocating Engine | Gas Turbine | Gas Turbine | Gas Turbine | Gas Turbine | Combined Cycle | Combined Cycle | Battery Storage | Battery Storage | Battery Storage
Fuel Type | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Grid Power | Grid Power | Grid Power
Output Capacity (kW) | 1000 | 3000 | 5000 | 10000 | 25000 | 40000 | 100000 | 375000 | 100 | 500 | 1000
Energy Capacity (MWh) | - | - | - | - | - | - | - | - | 400 | 2000 | 4000
Capacity Factor (%) | 91.32% | 91.32% | 91.32% | 91.32% | 93.61% | 93.61% | 93.61% | 93.61% | - | - | -
Hours of Operation (hrs) | 8000 | 8000 | 8000 | 8000 | 8200 | 8200 | 8200 | 8200 | - | - | -
Electric Heat Rate, HHV (Btu/kWh) | 9210.3391 | 8417.139 | 12428.8987 | 12205.3374 | 10060.3352 | 9624.8237 | 6785.3252 | 6269.2954 | - | - | -
Electric Efficiency, HHV (%) | 36.8% | 40.4% | 27.47% | 27.96% | 33.92% | 35.54% | 50.29% | 54.42% | - | - | -
Fuel Input (Btu/hr) | 9210.3391 | 25251.4169 | 62144.4934 | 122053.3736 | 251508.3809 | 384992.9478 | 678532.5175 | 2350985.7825 | - | - | -
Thermal Output (Btu/hr) | 4015.3919 | 10119.5144 | 27354.5787 | 59505.9357 | 84655.4275 | 133200.8803 | 344491.485 | 687014.5 | - | - | -
Total CHP Efficiency, HHV (%) | 78.7% | 78.8% | 67.63% | 68.1% | 69.3% | 69.76% | 65.37% | 63.21% | - | - | -
Power-to-Heat Ratio | 0.87 | 1.06 | 0.5825 | 0.6875 | 0.8975 | 1.03 | 1.6 | 1.87 | - | - | -
Net Heat Rate (Btu/kWh) | 4335.4511 | 4329.9492 | 5044.3542 | 5010.2898 | 4887.2152 | 4873.9794 | 5219.6298 | 4100.1531 | - | - | -
Equipment Lifetime (years) | 25 | 25 | 30 | 30 | 30 | 30 | 35 | 35 | - | - | -
Inverter Life (years) | - | - | - | - | - | - | - | - | 15 | 15 | 15
Cycles per Day | - | - | - | - | - | - | - | - | 1 | 1 | 1
Annual Energy Degradation | - | - | - | - | - | - | - | - | 0.5% | 0.5% | 0.5%
Battery Cell Life (years) | - | - | - | - | - | - | - | - | 10 | 10 | 10
Total Installed Cost ($/kW) | 3143.6 | 2778.2 | 2818.8 | 2115.1981 | 1728.0554 | 1502.165 | 1743.5787 | 1404.6118 | 3467.197 | 2919.9148 | 2646.5802
Equipment Cost ($/kW) | 1635.6 | 1160 | 1044 | 836.6042 | 746.0133 | 637.8962 | 628.6296 | 498.0853 | 1877.5056 | 1718.0876 | 1557.2566
BOP & Installation ($/kW) | 1508 | 1618.2 | 1774.8 | 1278.5939 | 982.0421 | 864.2688 | 1114.9491 | 906.5265 | 1589.6913 | 1201.8272 | 1089.3236
Variable O&M Costs ($/kWh) | 0.02242 | 0.01888 | 0.017168 | 0.014132 | 0.010599 | 0.01058 | 0.0046297 | 0.0036105 | - | - | -
Fixed O&M Costs ($/kW-year) | - | - | - | - | - | - | - | - | 86.6799 | 72.9979 | 66.1645
Sector | Industrial
Equipment | Total
Vintage | New
Year | 2018
Dollar Year | 2022
Size, Technology, & Configuration | Small_Recip_CHP | Large_Recip_CHP | Med_GT_CHP | Large1_GT_CHP | Large2_GT_CHP | Large3_GT_CHP | Small_CC_CHP | Large_CC_CHP | Small_Storage_Ind | Med_Storage_Ind | Large_Storage_Ind
Prime Mover | Reciprocating Engine | Reciprocating Engine | Gas Turbine | Gas Turbine | Gas Turbine | Gas Turbine | Combined Cycle | Combined Cycle | Battery Storage | Battery Storage | Battery Storage
Fuel Type | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Grid Power | Grid Power | Grid Power
Output Capacity (kW) | 1000 | 3000 | 5000 | 10000 | 25000 | 40000 | 100000 | 375000 | 100 | 500 | 1000
Energy Capacity (MWh) | - | - | - | - | - | - | - | - | 400 | 2000 | 4000
Capacity Factor (%) | 91.32% | 91.32% | 91.32% | 91.32% | 93.61% | 93.61% | 93.61% | 93.61% | - | - | -
Hours of Operation (hrs) | 8000 | 8000 | 8000 | 8000 | 8200 | 8200 | 8200 | 8200 | - | - | -
Electric Heat Rate, HHV (Btu/kWh) | 9208.7929 | 8413.4916 | 12637.167 | 12332.7986 | 10135.3032 | 9624.8237 | 6802.5092 | 6285.0428 | - | - | -
Electric Efficiency, HHV (%) | 36.81% | 40.42% | 27.01% | 27.67% | 33.67% | 35.63% | 50.16% | 54.29% | - | - | -
Fuel Input (Btu/hr) | 9208.7929 | 25240.4749 | 63185.8349 | 123327.9862 | 253382.5797 | 384992.9478 | 680250.924 | 2356891.0575 | - | - | -
Thermal Output (Btu/hr) | 4044 | 10250 | 27211.8527 | 60208.9357 | 85015 | 134180 | 345381.112 | 688925 | - | - | -
Total CHP Efficiency, HHV (%) | 78.5% | 78.6% | 67.58% | 68% | 69.3% | 69.3% | 65.24% | 63.18% | - | - | -
Power-to-Heat Ratio | 0.87 | 1.06 | 0.585 | 0.675 | 0.895 | 1.03 | 1.6 | 1.87 | - | - | -
Net Heat Rate (Btu/kWh) | 4346.4968 | 4340.9669 | 5047.3373 | 5017.6471 | 4895.2654 | 4888.2521 | 5230.1048 | 4102.0481 | - | - | -
Equipment Lifetime (years) | 25 | 25 | 30 | 30 | 30 | 30 | 35 | 35 | - | - | -
Inverter Life (years) | - | - | - | - | - | - | - | - | 15 | 15 | 15
Cycles per Day | - | - | - | - | - | - | - | - | 1 | 1 | 1
Annual Energy Degradation | - | - | - | - | - | - | - | - | 0.5% | 0.5% | 0.5%
Battery Cell Life (years) | - | - | - | - | - | - | - | - | 10 | 10 | 10
Total Installed Cost ($/kW) | 3151.115 | 2783.795 | 2947.168 | 2119.4072 | 1731.65 | 1505.2829 | 1753.5448 | 1406.1972 | 3637.1536 | 3084.3706 | 2789.9148
Equipment Cost ($/kW) | 1639.1909 | 1160.595 | 1113.92 | 838.269 | 747.838 | 639.4565 | 631.9484 | 498.6118 | 2030.9357 | 1863.8389 | 1664.4607
BOP & Installation ($/kW) | 1511.9242 | 1623.2 | 1833.248 | 1281.1382 | 983.812 | 865.8264 | 1121.5964 | 907.5855 | 1606.2179 | 1220.5317 | 1125.454
Variable O&M Costs ($/kWh) | 0.02244 | 0.018899 | 0.01734 | 0.01516 | 0.011162 | 0.01106 | 0.0048397 | 0.0037743 | - | - | -
Fixed O&M Costs ($/kW-year) | - | - | - | - | - | - | - | - | 90.9288 | 77.1093 | 69.7479
Sector | Industrial
Equipment | Total
Vintage | New
Year | 2015
Dollar Year | 2022
Size, Technology, & Configuration | Small_Recip_CHP | Large_Recip_CHP | Med_GT_CHP | Large1_GT_CHP | Large2_GT_CHP | Large3_GT_CHP | Small_CC_CHP | Large_CC_CHP | Small_Storage_Ind | Med_Storage_Ind | Large_Storage_Ind
Prime Mover | Reciprocating Engine | Reciprocating Engine | Gas Turbine | Gas Turbine | Gas Turbine | Gas Turbine | Combined Cycle | Combined Cycle | Battery Storage | Battery Storage | Battery Storage
Fuel Type | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Grid Power | Grid Power | Grid Power
Output Capacity (kW) | 1000 | 3000 | 5000 | 10000 | 25000 | 40000 | 100000 | 375000 | 100 | 500 | 1000
Energy Capacity (MWh) | - | - | - | - | - | - | - | - | 400 | 2000 | 4000
Capacity Factor (%) | 91.32% | 91.32% | 91.32% | 91.32% | 93.61% | 93.61% | 93.61% | 93.61% | - | - | -
Hours of Operation (hrs) | 8000 | 8000 | 8000 | 8000 | 8200 | 8200 | 8200 | 8200 | - | - | -
Electric Heat Rate, HHV (Btu/kWh) | 9206.0357 | 8410.6947 | 12912.0151 | 12479.883 | 10264.7413 | 9624.8237 | 6838.1958 | 6372.1095 | - | - | -
Electric Efficiency, HHV (%) | 36.83% | 40.43% | 26.42% | 27.34% | 33.24% | 35.96% | 49.9% | 53.55% | - | - | -
Fuel Input (Btu/hr) | 9206.0357 | 25232.0842 | 64560.0757 | 124798.8296 | 256618.5319 | 384992.9478 | 683819.5759 | 2389541.0666 | - | - | -
Thermal Output (Btu/hr) | 4320 | 10670 | 28114.9827 | 60357.9316 | 85230 | 135760 | 347100 | 694032.3 | - | - | -
Total CHP Efficiency, HHV (%) | 78.4% | 78.3% | 67.55% | 68% | 69.3% | 68.8% | 64.93% | 62.62% | - | - | -
Power-to-Heat Ratio | 0.87 | 1.05 | 0.59 | 0.65 | 0.89 | 1.03 | 1.6 | 1.85 | - | - | -
Net Heat Rate (Btu/kWh) | 4352.0408 | 4357.599 | 5051.0733 | 5017.6471 | 4838.9407 | 4959.1582 | 5255.1205 | 4129.52 | - | - | -
Equipment Lifetime (years) | 25 | 25 | 30 | 30 | 30 | 30 | 35 | 35 | - | - | -
Inverter Life (years) | - | - | - | - | - | - | - | - | 15 | 15 | 15
Cycles per Day | - | - | - | - | - | - | - | - | 1 | 1 | 1
Annual Energy Degradation | - | - | - | - | - | - | - | - | 0.5% | 0.5% | 0.5%
Battery Cell Life (years) | - | - | - | - | - | - | - | - | 10 | 10 | 10
Total Installed Cost ($/kW) | 3182.0016 | 2799.8 | 3350.625 | 2509.52 | 1927.86 | 1584.96 | 1765.12 | 1426.88 | 4821.9088 | 4017.5766 | 3444.3706
Equipment Cost ($/kW) | 1754.2206 | 1256.2 | 1266.4118 | 992.5666 | 832.5741 | 673.304 | 632.8 | 506.24 | 3093.8106 | 2801.3514 | 2270.6512
BOP & Installation ($/kW) | 1427.781 | 1543.6 | 2084.2132 | 1516.9534 | 1095.2859 | 911.656 | 1132.32 | 920.64 | 1728.0982 | 1216.2252 | 1173.7194
Variable O&M Costs ($/kWh) | 0.021503 | 0.018108 | 0.017344 | 0.015164 | 0.011165 | 0.011063 | 0.0048409 | 0.0037752 | - | - | -
Fixed O&M Costs ($/kW-year) | - | - | - | - | - | - | - | - | 120.5477 | 100.4394 | 86.1093
Sources | DOE CHP Fact Sheet Series, Packaged CHP eCatalog | DOE CHP Fact Sheet Series, Packaged CHP eCatalog, Develop Data Sheets | DOE CHP Fact Sheet Series, Packaged CHP eCatalog, Develop Data Sheets | DOE CHP Fact Sheet Series, Packaged CHP eCatalog, Develop Data Sheets | DOE CHP Fact Sheet Series, Packaged CHP eCatalog, Develop Data Sheets | DOE CHP Fact Sheet Series, Packaged CHP eCatalog, Develop Data Sheets | DOE CHP Fact Sheet Series, Packaged CHP eCatalog, Develop Data Sheets | DOE CHP Fact Sheet Series, Packaged CHP eCatalog, Develop Data Sheets | NREL Storage Cost Benchmarks, DNV Battery Cost Library | NREL Storage Cost Benchmarks, DNV Battery Cost Library | NREL Storage Cost Benchmarks, DNV Battery Cost Library